| Daily Maintenance Checklist |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | Mon | Tues | Wed | Thurs | Fri | Sat | Sun |
| Date |  |  |  |  |  |  |  |
| Technician Initials |  |  |  |  |  |  |  |
| Visual Inspections | Indicate Y (Yes) or N (No) in the spaces provided below |  |  |  |  |  |  |
| Have all combustible materials been removed from the in and around the PSA plant? |  |  |  |  |  |  |  |
| Has the floor and surfaces been mopped and dusted? |  |  |  |  |  |  |  |
| Is the PSA plant free of any physical damage? |  |  |  |  |  |  |  |
| Are cylinders stored safely? (with caps and chains) |  |  |  |  |  |  |  |
| Are all ventilation systems working, including fans? |  |  |  |  |  |  |  |
| Are air intake filter mats, intake cover, and ventilation filters in place? |  |  |  |  |  |  |  |
| Is the inlet air filter in good condition? |  |  |  |  |  |  |  |
| Are the air compressor and equipment housing covers in place? |  |  |  |  |  |  |  |
| Is the air compressor motor belt free of any visible damage (if equipped)? |  |  |  |  |  |  |  |
| Is the air compressor oil level at the manufacturer’s specified level? |  |  |  |  |  |  |  |
| Is the bottom of the air compressor free from any signs of oil leakage? |  |  |  |  |  |  |  |
| Is the air compressor condensate draining correctly? |  |  |  |  |  |  |  |
| Have the condensate containers been emptied (if equipped)? |  |  |  |  |  |  |  |
| Is the air dryer condensate draining correctly? |  |  |  |  |  |  |  |
| Are the in-line filters’ condensate draining correctly? |  |  |  |  |  |  |  |
| Is the air tank condensate draining correctly? |  |  |  |  |  |  |  |
| Is the booster compressor operating without unusual noises or leaks (water and oil)? |  |  |  |  |  |  |  |
| If the backup manifold has not been used in the past day, does the pressure gauge indicate it is maintaining pressure? |  |  |  |  |  |  |  |
| Are the manifold pigtails in good working condition? |  |  |  |  |  |  |  |
| Check the status of the fire detection and suppression system. Are they in good working condition? |  |  |  |  |  |  |  |
| Data Collection | Mon | Tues | Wed | Thurs | Fri | Sat | Sun |
| Record the temperature in PSA plant room or container (°C) |  |  |  |  |  |  |  |
| Are there any alarm codes? If so, identify components and take a picture of the alarm. |  |  |  |  |  |  |  |
| Record the air compressor temperature (°C) |  |  |  |  |  |  |  |
| Record the air compressor running hours |  |  |  |  |  |  |  |
| Record the PDP temperature (°C) |  |  |  |  |  |  |  |
| Record the oxygen purity (%) - PLC |  |  |  |  |  |  |  |
| Record the oxygen purity (%) using a handheld oxygen analyzer |  |  |  |  |  |  |  |
| Record the oxygen generator running hours |  |  |  |  |  |  |  |
| Record the booster compressor running hours |  |  |  |  |  |  |  |
| Record the booster compressor pressure gauge readings (list every stage) and temperature (once/week) | Inlet Pressure: Inlet Temp: 1st Stage Pressure: 1st Stage Temp: 2nd Stage Pressure: 2nd Stage Temp: 3rd Stage Pressure: 3rd Stage Temp: Exhaust Pressure: Exhaust Temp: |  |  |  |  |  |  |
| Enter the number of cylinders filled for your standard cylinder size. Indicate standard cylinder size_______[L] |  |  |  |  |  |  |  |
| Record the number of hours during which cylinders were filled. |  |  |  |  |  |  |  |
| Compare the running hours recorded above with the Preventive Maintenance Schedule. Is service needed? |  |  |  |  |  |  |  |